# TENDER 16-20

WATER TREATMENT BUILDING

ADDENDUM NO. 3

September 30th, 2016

This addendum forms part of the Tender Documents and shall be read, interpreted, and coordinated with all other parts. The costs of all elements contained herein shall be included in the submission. The following revisions, changes, corrections, additions, and or deletions supersede the information contained in the original Documents to the extent referenced and shall become part thereof.

Addendum Item 1

Questions & Answers

- Proponent Question: 14

There does not appear to be a pay item for the 3 flowmeters on C202 & C304.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

Tender item 33.2 “Welded steel pipe -250 mm diam……..” does not appear on the plans, however there is 250 mm PVC on C202 with no pay item. Which is correct, steel or PVC?

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

Tender items 33.3 and 33.4 quantities are double what is on the plans sheet C202. In order to calculate representative unit prices the quantities should be closer to actual field measurement.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

There is no pay item for 900 mm welded steel pipe. There is 4 LM showing on C202.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

Tender item 33.8 “Tee 300x300x250 HxHxF” should be a HxFxF configuration to correspond to item 20 on C202.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

Item 33.16 “”Wye – 1200F x 1200F x 900F” is incorrectly configured. As per item #1 on C202 it should be “Tee - 1200W x 1200W x 900W”.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

The following 8 bid items do not appear on the plans or correspond with any work scope of the project; 33.9, 33.12, 33.13,  33.14,  33.15,  33.17,  33.18, and  33.19.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 14

There are 14 various types of water fittings and valves on C202 that do not have pay items in the Form of Tender which are as follows;

- Tee 1200W x 900F x 500F

- Tee 1200W x 1200W x 900W

- Tee 900W x 760F x 250F

- Blind flange – 500 mm

- Gate Valve – 250 mm F x H

- Gate Valve – 760 mm F x F

- Cap 500 mm

- Cap 760 mm

- Bend 250 mm 45 deg H x H

- Bend 250 mm 22.5 deg H x F

- Bend 250 mm 11.25 deg H x F

- Bend 300 mm 30 deg H x H

- Bend 500 mm 45 deg W x W

- Bend 760 mm 64.3 deg W x W.

Response:

Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 9

On the tender form pages 14 of 22, 26 - Electrical I believe items 26.7 and 26.8 are redundant because they are covered by 25.1.

Response:

Line items 26.7 and 26.8 should not be populated, relying only on 25.1. Delete the original Appendix 1A Detailed Schedule of Quantities and Prices  and replace with Appendix 1A (Revised September 30th, 2016) as attached with this addendum.

- Proponent Question: 9

Can division 25 09 01 thru to 25 09  94 be shown on the tender form as DDC BMS control to ensure it is clear that the PLC + instrumentation is clearly different than the BMS.

Response:

Clarification: In appendix 1A the price breakdown noted under 23.8 Controls refers to the HVAC controls system detailed in spec sections 250901, 250913, 250922, 250993 and 250994. The price breakdown noted under 25.3 Control panels refers to the Process controls detailed in spec sections 250501, 251400, 253101 and 259000.

- Proponent Question: 12

Request for alternate products from SOPREMA as follows:

DIVISION 7: Section 07 13 27 

2.1.1 : Horizontal:Grace Preprufe 300R by Grace Construction Products. 

Alternate: SOPREMA COLPHENE BSW-V 

2.1.2 : Vertical: Grace Preprufe 160R by Grace Construction Products. 

Alternate: SOPREMA COLPHENE BSW-H

DIVISION 7: Section 07 14 00 

2.1.1 : Procor® fluid applied membranes by Grace Construction Products 

Alternate: SOPREMA COLPHENE 3000 (Self adhesive membrane) or SOPREMA COLPHENE Torch N Stick (Torch applied membrane for high water table situations and or hydrostatic pressure)

Response:

Section 07 13 27 alternates: approved provided it meets the performance and testing requirements of the specification.

Section 07 14 00 alternates: not approved. Fluid applied required.

- Proponent Question: 14

Please provide a detail for the Air Valve, Tender Item 33.27.

Response:

Model number has been provided and is sufficient.

- Proponent Question: 14

What is the size of the air release valves in the 3 flowmeter chambers as shown on C304?

Response:

Model number has been provided and is sufficient.

- Proponent Question: 15

Can I request shop drawings and BOM for the vertical turbine pump package?

Response:

Not available.

- Proponent Question: 17

Please confirm the extent of the Owner supplied 1200mm and 1000mm steel watermains. Please confirm if they will be supplied with coatings and the contractor will only be responsible for the site applied coatings at the weld locations. Is the 760mm  pipe also Owner supplied?

Response:

No pipe is owner supplied. All pipes and associated coatings to be provided by contractor under this scope of work.

- Proponent Question: 17

Door 003 is missing from the door schedule.

Response:

Door 003:

Size: 915x2135

Type: painted hollow metal door and frame c/w sidelight (450mm wide x height of door c/w 10mm single glazing)

Hardware:  function - store room

hardware – butt hinges, closer, door stop

- Proponent Question: 17

Please confirm the project specific specified U-Value of 1.75 W/m2*K will need to be confirmed via computerized thermal modelling.

Response:

Based on Ashrae 90.1 for zone 4 buildings, a U value of 2.84W/m2*k is the required thermal resistance for the glazing system and can be used when designing window systems. Computerized modelling not required.

- Proponent Question: 17

We’d like to propose Alumicor 2600 Thermawall for the curtainwall, an alternate to Kawneer 1600. Please note Kawneer 1600 1-2 will not meet the specified U-Value.

Response:

Approved.

- Proponent Question: 17

Please confirm the sealed unit make-up. Will PPG industries be an approved alternate supplier of LOW E coatings?

Response:

Yes.

- Proponent Question: 17

Please confirm the glass make-up for the interior curtainwall windows.

Response:

10mm single pane safety glass

- Proponent Question: 17

Please confirm class 1 clear anodized finish is correct.

Response:

Colour to be confirmed through standard colour range during shop drawing process.

- Proponent Question: 19

Is a Door Hardware Schedule is going to be issued for SECTION 08 71 00?

Response:

Hardware schedule is on drawing is on A002.

- Proponent Question: 20

With reference to Drawing C202 please provide profiles for Connection Details 1 and 2. Specifically we need to determine where the new 900 mm steel, 760 mm steel, 250 mm PVC, and 100 mm PVC drain are to be installed relative to the existing mains on  Detail 1. Similarly  for Detail 2 please provide a profile showing new installation relative to existing supply mains.

Response:

Question received and will be responded to in Addendum No. 4

- Proponent Question: 20

In order to facilitate a video inspection of the entire supply main we will have to access manway hatches on previously installed works. Please provide a plan/profile of the existing 1200 / 1000 mm mains showing the hatch locations.

Response:

Only section requiring video would be the new sections installed provided the contractor has some means of securing any exposed openings at the end of each working shift so as to not allow any wildlife to get in there.

- Proponent Question: 22

Detail 1 on Drawing C105 indicates that the 1000mm Dia Steel Water Main is owner supplied, there is a note on drawing C201 indicating that the 1200mm Dia Steel Water Main is owner supplied – can you please confirm that the steel water main is owner supplied?  If the steel pipe is owner supplied please provide shop drawings and a list of the fittings that will be provided?  This will be required to determine the scope for welding and coating.

Response:

No pipe is owner supplied. All pipe and fittings to be provided by contractor under this scope of work.

- Proponent Question: 22

Item 1.2.5 of Section 01 12 00 states “Once contract 1 is complete, or near a state of completion, a survey of the site will be conducted by the City and the information provided to the contractor. This information will be made available as an addendum”.  Is a recent site survey available to assist in determining the extent of site clearing/stripping and excavation required?

Response:

Existing conditions drawing has been provided in Addendum 3.

- Proponent Question: 22

Is an as-built drawing available for the exisiting steel watermains that are to be tied-in to?

Response:

No.

- Proponent Question: 23

For the emergency generator for the above mentioned tender, could you please advise which payment item in division 26 – Electrical should we place the emergency generator in?  As there is separate payment item for PLC’s, MCC/VFD’s.  it’s not very clear which item we should put the cost of the emergency genset.  Item 26.6 Power or should it be in a separate item?

Response:

This contract form is a CCDC 2 Stipulated Price contract. Tenderer is only required to submit completed Appendix 1 with tender submission.

Appendix 1A is required to be completed and submitted by the successful tenderer post award and will be used for processing progress claims. Backup generator, complete has been added to Appendix 1A as attached.

- Proponent Question: 24

The answer to Proponent Question 11 in Addendum 2 says the top of concrete wall is to be 400mm above the steel angle support and to match the top of concrete elevations shown on the elevations. If the 400mm requirement is to be met, the top of concrete must be 400mm higher than shown on the elevations. The question that was previously answered was related to GL 1 and 5, but the response prompts the following question regarding GL A: 3/S102 and 4/S102 shows the top of concrete on the south elevation to be 142.20. Does this need to be revised to 142.60 to be 400mm above the angle?

Response:

The top of concrete on GL A is at 142.2 as shown

- Proponent Question: 24

How is the stainless steel L100x75x6.4 LLV for the trench grating installed along GL A into the foundation wall? How about at the concrete cross beams?

Response:

The grating is not required to be connected to the concrete beams or foundation wall.

- Proponent Question: 24

Detail 4/A404 is incorrect. There is a trench with grating directly next to the overhead door. If the OH door is installed on top of the grating, air will constantly flow into the building.

Response:

Add 300mm x 200mm thick x 3000mm wide cantilievered concrete slab at o/h door location to provide a solid surface for the door to close onto.

- Proponent Question: 24

Detail 4/A403 is missing the trench.

Response:

Will be updated for IFC set

- Proponent Question: 25

4/S102 says the max height of retained soil is 3000mm. The max height of soil required appears to be 3560mm based on the proposed grades.

Response:

The detail on 4/S105 should indicate a maximum height of soil of 3600.

- Proponent Question: 25

Please confirm that cable/conduit and wire P1, P2, P3, P1A, P1B, P1C, P1D and Telus U/G conduits into the water treatment building are all outside of the electrical contractor’s scope of work. If it is with-in the electrical contractors scope of work please provide conduit and wire/cable sizes.

Response:

- P1, P2, P3 conductors not currently in scope of work for Contractor. Contractor is responsible for coordinating with BC Hydro. BC Hydro will be the installer and supplier of P1, P2, P3 conductors, complete HV primary cable system and transformer. Reference E101 Note 12. Contractor responsible for supplying and installing P1, P2, P3 conduit. Contractor to assume 100mm DB2 Duct for each identified secondary conduit (three in total per the current design). BC Hydro will update requirements once final approvals are achieved. Current design does not show concrete encasement.

- Drawing E101 revised to remove reference to P1A, P1B, P1C, P1D, and correctly identify P1, P2 and P3.

- Telus U/G conduit will be the responsibility of the Contractor. Reference E101 Note 12; assume 53mm DB2 Duct from site boundary to electrical room.

- Coordinate city communication conduit extension detailed on C103, Construction note 2.

- Proponent Question: 25

Please clarify/identify what conduit or cable feeding the waste pump control station as shown on drawing E101.

Response:

Drawing E101 has been revised to identify Cable S61 and the proper routing of this cable. Note that additional cables are required between the waste tank and the electrical room, not specifically shown on E101.

- Proponent Question: 25

Please confirm location of P-400 VFD and P-401 VFD.

Response:

VFDs for P-400 and P-410 supplied by chemical dosing supplier. VFDs to be installed by the Contractor directly beside the dosing skid for P-400 and P-410, shown on E301, east wall, Process 2 area.

- Proponent Question: 25

Drawing E301, grid lines 3 & C-B, there is a PLC cabinet shown. Please confirm if this is OSHG PLC or MCP-100. If this is MCP-100, please clarify the location of the OSHG PLC or vice-versa.

Response:

The location identified in the question references MCP-100. OSHG PLC cabinet supplied and installed on the NaOCl generator skid, and is located at the point identified by all other instrument bubbles for the NaOCl skid (interior east wall of Process 2 area).

- Proponent Question: 26

Request for Wayne Dalton Rolling Steel as an alternative Rolling Steel Manufacture for this project.

Response:

Approved.

- Proponent Question: 27

Can you provide a contact for Calgon?

Response:

Refer to the response to Addendum No. 2, question #43.

- Proponent Question: 27

Can Calgon’s scope of work become a PC Sum?

Response:

Calgon will bill the Owner directly for their required attendance as such the Contractor should not carry any allowance for Calgon commissioning/site expenses.

- Proponent Question: 28

It appears that existing grade elevations do not match existing elevations provided on the Civil drawings. As we do not have full access to the site at this time please confirm these elevations are accurate.

Response:

Existing conditions drawing has been provided in Addendum 3

- Proponent Question: 28

It would appear the Caisson transitions from circular to square at an approximate elevation of 137. Will the Caisson be backfilled to approximate elevation of 142, or will 2 sides be left at 137?

Response:

Caisson will be backfilled to elevation 142.

- Proponent Question: 28

Is there any intention to leave existing sediment control in place & handed over to the General Contractor? Including the sediment fence at lakes edge and the floating boom in lake.

Response:

Sediment fencing in place for current contract will be removed.

- Proponent Question: 28

Please clarify if it is the intent to have the Preprufe 160r on the foundation wall along GL-A. This wall makes up part of the trench where this product is shown under slab and behind the walls on structural detail 2/S102. Architectural drawings appear to show the Procor product as the waterproof membrane along GL-A, please clarify which product is to be used on GL-A.

Response:

Procor can be used for all foundation wall waterproofing as outlined in the spec. 07 14 00

- Proponent Question: 29

It appears from the proponent questions in Addendum 2 that some Contractors are interpreting this as a Unit Price contract. My understanding was that Appendix 1A was presented for information only and bids are not to be based on the quantities provided as this is a Stipulated Sum contract. Please confirm which is correct.

Response:

This contract form is a CCDC 2 Stipulated Price contract. Tenderer is only required to submit completed Appendix 1 with tender submission.

Appendix 1A is required to be completed and submitted by the successful tenderer post award and will be used for processing progress claims.

- Proponent Question: 30

Regarding ISO 9000 cert – requesting that SPFA (Steel Plate Fabricators Association) be allowed as a quality management program in lieu of, in addition to,  ISO.

Response:

ISO 9000 shall be met.

- Proponent Question: 30

Regarding B.C. Boiler Safety Welder Certificate – requesting that welders certified to perform work to ASME BPVC standards are acceptable in lieu of the Canadian standard.

Response:

ASME BPVC is acceptable

- Proponent Question: 30

Regarding the No. 4 finish for the SST piping - is this to be on the ID, OD, or both?

Response:

Both.

- Proponent Question: 31

Can the tender closing be extended so the radio supplier has time to quote?

- Complete a line of site study

- Engineer the wireless link

- Confirm if a radio tower needs to be built for line of site, price if required

- Complete Seismic study on the 911 tower

- Get BC Hydro approval  for access to their tower

Response:

In regards to the closing date, refer to Addendum, Item 2 below.

- A visual line of site was confirmed between the two locations with equipment detailed in specification 270513.

- Supplier to price the work based on the information provided, including the requirement to engineer the specific link installations and implementation requirements.

- Supplier to price work based on the information provided.

- If the use of the 911 tower necessitates a seismic study, the supplier to price into the scope of work. The proponent will provide pricing for the work based the ability to install the equipment based on the information provided.

- Supplier to price work based on the information provided. Project scope of work does not include modifications to communication equipment on the Hydro Surge Towers at this time. Please provide pricing based on the information contained within the documentation provided

- Proponent Question: 32

Will the equipment on the surge towers be abandoned in place and left for demolition with the surge towers?

Response:

Project scope of work does not include modifications to communication equipment on the Hydro Surge Towers at this time. Please provide pricing based on the information contained within the documentation provided.

- Proponent Question: 33

On drawing A101 in LAB 003 shows a door with a sidelight frame but this is not on the door schedule. What type of door and frames is this?

Response:

See question 75.

- Proponent Question: 34

Drawing C103, item 2 appears to be a 75mm duct for communications. This doesn’t show up on the electrical drawings. Please confirm if this is part of the electrical scope of work.

Response:

This is part of the electrical scope of work.

- Proponent Question: 34

I cannot find BBH 4, 5 & 6 on electrical drawings. Please confirm location.

Response:

BBH 4,5 and 6 are no longer part of the design. A future addendum will resolve this conflict in the drawings.

- Proponent Question: 34

Please identify location point of electrical connection for crane motors 1, 2 & 3.

Response:

A future addendum will be submitted to identify the location of this tie point.

- Proponent Question: 34

Please confirm location of that CP-501, CP-511 and future location of CP-521.

Response:

CP-501, CP-511 and future CP-521 to be installed against the dividing wall of the electrical/process area, on the process side of the wall.

- Proponent Question: 34

Please confirm that UV-501 Panel, CP-501, UV-511 Panel & CP-511  are part of the existing, relocated ultra violet disinfection reactor system.

Response:

CP-501/511 and the relating UV reactors and instrumentation is part of the existing equipment being relocated. Cabling between the equipment to be replaced. Re-Commissioning of the equipment is included in the scope of the Contractor.

- Proponent Question: 34

Cable schedule has identified a piece of equipment as LP-C. I cannot find this on the floor plan. Please clarify.

Response:

Question is not clear; if the reference is Panelboard C (LP-C), this panel distributed UPS power, and is located in the electrical room.

- Proponent Question: 34

Please confirm location of LCP-901.

Response:

Reference C-103. LCP-901 located on the south side of the parking lot, near the utility transformer.

- Proponent Question: 34

Drawing E101 note 9 references drawing C303. Drawing C303 shows three 50mm RPVC conduits that are not shown on the electrical drawings. It also talks about the Sanitary Storage Tank being shipped to site loose and electrical work to be completed by contractor. The electrical drawings seem to indicate that the electrical contractors scope of work ends at JB-901. If there is any electrical work to be done between JB-901 and the P-901 please identify the electrical scope of work along with the three 50mm conduits in question

Response:

The contractor is responsible for wiring, testing and commissioning the electrical and controls portion of the sanitary storage tank. Reference the cable schedule, single line diagram, control panel drawings and C303 to provide a functional system.

- Proponent Question:  36

Request for American Specialties Inc. as an alternative for washroom accessories..

Response:

Provided in spec 102810

- Proponent Question: 37

Can Simson-Maxwell be added to the list of approved suppliers for the generator/e-house/switchgear supply (263213.2.12.1)?

Response:

Yes, but the Contractor must provide a unit which works within the current design spatial limits set out on the drawings.

- Proponent Question: 38

The actuator is on P&ID number P009 and has tag FCV-604. Do you know what valve this actuator is being put on, have any information about it or have the actuator spec? We will need to know this to size the actuator. I’m assuming they will want this actuator to be the same as the other assembly (tag FCV-501).

Response:

Electrical spec for actuator provided for the valve FCV-604. The valve is shown, as he mentioned on drawings P009 and is provided by the city. This actuator is not related to valve FCV-501 which is supplied with actuator as a part of UV relocation package.

- Proponent Question: 38

Specification is calling for an odour control unit with fan in an aluminum enclosure – is there any more information on this odour control unit? The only odour control unit our supplier uses is the FRP unit without a fan.

Response:

Will be responded to in Addendum 4.

- Proponent Question: 38

Please provide the Valve Spec No. for BFV-811, FCV-820 and FCV-830 in the Process Valve list, Section 40 06 23.

Response:

Specification section is now updated. These valves will be provided by the supplier of the compressed air system and as such do not require our specification table.

- Proponent Question: 38

Trolley cranes and beams are shown on the plan drawings – are these included in this tender? Please provide specification if required.

Response:

Question received and will be responded to in Addendum No. 4

- Proponent Question: 38

On drawing A101 in LAB 003 shows a door with a sidelight frame but this is not on the door schedule. What type of door and frames is this?

Response:

See question 75.

- Proponent Question: 38

Door type D2 is referenced as a solid wood core door on the door schedule (DWG 15-508-A002), the specifications only refer to metal doors and frames (081113) and overhead coil (08330). Are there specifications related to wood doors and frames?

Response:

Door construction:

39mm LVL (laminated veneer lumber) core

3mm veneer plywood to each side

Solid 16mm KD vertical grain cedar

#1 T edge

Polyurethane glue

Supplier: Delta Door"

- Proponent Question: 39

With reference to Drawing C102 and Sections A,B,C/C104 it appears existing ground as drawn is considerably higher than what we are seeing in the field. It is our understanding the contractor currently working at the site has taken the grade down to approximately elevation 142.0 in some areas but not the entire building envelope. Can we get a plan or sections that show where the site subgrade will be at commencement of this contract.

Response:

Existing conditions drawing has been provided in Addendum 3

- Proponent Question: 39

The detail for the flow meter chambers on C304 shows mechanical couplings and restraint on each side of the chambers. The distance from the chamber to adjacent fittings (tees and bends) is close enough that we can provide continuous piping flange to flange without the couplings and  restraints. Would this be acceptable?

Response:

Couplings and restraints should be provided as shown on the drawings.

- Proponent Question: 39

The detail on C302 for the blowdown shows 300mm pipe and 200mm gates and check valve. Please clarify.

Response:

Drawing has been updated to reflect 300mm valves

- Proponent Question: 39

What is the depth / floor elevation for the blowdown?

Response:

Drawing has been updated to reflect 1.0m (MIN) cover

- Proponent Question: 39

The blowdown inlet pipe calls for a SS thrust ring welded to the schedule 40 pipe. Is the pipe to be SS or can the thrust ring be carbon steel?

Response:

Stainless steel.

- Proponent Question: 40

Would request for alternate for Air Bloc 31 – Section 07 27 10.

Response:

Approved.

- Proponent Question: 40

Since the final tie-ins at the existing John Hart Water Quality Centre will take place after the new plant has been fully commissioned, please confirm the tie-ins will be excluded from the determination of substantial completion.

Response:

The work connecting the new watermain to the existing 500 Steel watermain is required to be complete by Substantial Completion so as to be able to facilitate the operation of the entire new system during the commissioning phase. The tie in to the existing 760 steel watermain and existing 250 PVC watermain can occur after Substantial Performance.

Addendum Item 2

Tender Closing Date Revision

Change Tender closing date from “Friday October 7th, 2016” and replace with “Thursday October 20th, 2016”.

Addendum Item 3

Delete and Replace Supplementary Specification Construction Schedule & Progress Reports Section 01 31 00, 1.3.2 Schedules

Delete Section 1.3.2 and replace as follows:

Show completion time and all specific dates and sequencing requirements. Identify activities making up the critical path. Schedule to include the following milestones:

Construction anticipated to commence No later than: November 30th, 2016

Substantial Performance of Contract to be achieved on or before: December 31st, 2017

Addendum Item 4

Revise Section 27 05 13, Section 1.1.4

Revise Section 27 05 13, Clause 1.1.4 to read: “The contractor will be responsible for engaging North Island Communications, Victoria Mobile Radio or another communications supplier familiar with the radio communication network used by the City of Campbell River to provide the following:”. All other sub clauses below 1.1.4 to remain unchanged.”

Addendum Item 5

Add Section 26 05 63 Motor & Valve Actuators

Add Section 26 05 63 Motor and Valve Actuators as attached to Tender package.

End of Addendum

Acknowledgement of this Addendum in your Tender submission is required.

Clinton J. Crook, SCMP, CPSM

Senior Buyer